KNX presence detector; false ceiling installation, pure white (PlanoCentro EWH-A-KNX)

- Passive infrared (PIR) presence detector fir false ceiling installation; flush fitting; integrated part 100x100mm; material strength up to 26 mm; two light channels for controlling two lighting groups; switching or constant light control; can be operated semi or fully automatically; channel brightness with cyclical output; channel for room monitoring; reduction of lighting time delay in event of brief absence; mixed light measurement 5-2000 lx,; square 360° detection area max. moving range 100m2 (10x10 m) stationary 64m2 (8x8 m) at 3.5m installation height; Light- switch-off delay auto-learning 30 s...60 min, switching between 2 brightness set point values, brightness set point values can be adjusted via bus, standby function; presence channel with switch-on delay 10 s...30 min / inactive, switch-off delay 10 s...120 min; parameters can be set and read remotely (SendoPro 868-A), Master/Slave mode option; test functions; scene control with two scenes, 8-bit scenes; pure white front frame 112 x112 x 5 mm, installation depth 80 mm; IP 40 protection rating; integrated bus coupling unit and power supply via bus.

Excluding install and start up.

Make: thebenHTS

Type: PlanoCentro EWH-A KNX, white

Order no.: 2059102

Unit: ST

Accessories:

# Management remote control (SendoPro 868-A)

Optional for the installer for start-up or adjustment to an application. Text-based operator guidance in the display. Transmission of individual settings or complete configuration sets to the detector possible. Saving and calling up user-defined parameter sets on internal memory or SD card. Fits all remote-controlled ThebenHTS presence detectors.

Order no.: 9070675

SendoClic user remote control

optional

Order no.: 9070690